## Pump Datasheet
CENTRIFUGAL PUMP DATASHEET
Model PWRI-220 ¦ Produced Water Reinjection Service
Parameter | Value | Unit
GENERAL INFORMATION
Tag Number | P-7402A
Service | Produced Water Reinjection Circulation
Manufacturer | TBD - Vendor
Model | PWRI-220
Type | Horizontal, End-Suction, Single Stage
PO Number | PO-2026-0742
Project | North Platform Reinjection Debottleneck
PROCESS / HYDRAULIC DATA
Rated Flow | 265 | m³/h
Rated Head | 47.7 | m
NPSH Available | 9.1 | m
NPSH Required (max) | 4.5 | m
Minimum Continuous Flow | 70 | m³/h
BEP Flow | 238.5 | m³/h
Suction Pressure | 2.5 | bar g
Discharge Pressure | 7 | bar g
DESIGN CONDITIONS
Design Pressure | 16 | bar
Design Temperature | 80 | °C
Operating Temperature | 35 | °C
MECHANICAL DATA
Rated Speed | 2980 | RPM
Max Allowable Speed | 3100 | RPM
Driver | Electric Motor, 75 kW, 380V, 50Hz
Impeller Diameter | 280 | mm
Impeller Type | Closed, 6-vane
Coupling | Flexible disc, spacer type
Weight (dry) | 850 | kg
MATERIALS OF CONSTRUCTION
Casing Material | ASTM A216 WCB
Impeller Material | ASTM A743 CF8M
Shaft Material | AISI 4140
Mechanical Seal | Cartridge type, API Plan 11
Bearing Type - DE | 6316 C3 Deep Groove Ball
Bearing Type - NDE | 6314 C3 Deep Groove Ball

## Test Requirements
FACTORY ACCEPTANCE TEST REQUIREMENTS
PWRI-220 ¦ Tag P-7402A ¦ Per API 610 / ISO 13709
Test | Required | Acceptance Criteria | Reference Standard
Hydrostatic Test | Yes | 1.5x design pressure, hold 30 min, no leaks | API 610 / ISO 13709
Performance Test | Yes | Head ±2%, Flow ±2% of rated, Eff within 3% | API 610 Cl. 8.3.3
NPSH Test | Yes | NPSHr per ANSI/HI 14.6 | API 610 Cl. 8.3.3.4
Mechanical Run Test | Yes | Min 4 hours, vibration per Table 8 | API 610 Cl. 8.3.4
Bearing Temperature | Yes | Max 82°C or ambient +45°C | API 610 Cl. 8.3.4
Vibration - Overall (unfiltered) | Yes | ≤ 3.8 mm/s RMS (for BH vibration) | API 610 Table 8
Vibration - Discrete Frequency | Yes | ≤ 2.5 mm/s peak (any discrete freq) | API 610 Table 8
Noise Level | Optional | ≤ 85 dBA at 1m | API 610 Cl. 8.3.4
Residual Unbalance | Yes | Per ISO 1940 G6.3 | API 610 Cl. 6.10
Shaft Runout | Yes | ≤ 0.025 mm TIR | API 610 Cl. 6.3

## Performance Curve Data
PERFORMANCE CURVE DATA
PWRI-220 ¦ Impeller Ø280 mm ¦ 2980 RPM ¦ Water @ 35°C
Flow (m³/h) | Head (m) | Efficiency (%) | Power (kW) | NPSHr (m)
0 | 60.32 | 0 | 24.75 | 1.89
53 | 58.76 | 32 | 26.51 | 1.99
106 | 56.16 | 55 | 29.48 | 2.31
159 | 53.04 | 70 | 32.78 | 2.94
212 | 49.4 | 79 | 36.08 | 3.57
238.5 | 47.32 | 82 | 37.51 | 3.99
265 | 44.72 | 80 | 40.15 | 4.41
291.5 | 41.08 | 76 | 43.01 | 5.35
318 | 36.4 | 70 | 44.88 | 6.83
Green row = BEP (225 m³/h) ¦ Blue row = Rated point (250 m³/h)
Data per API 610 / ISO 13709. Shutoff to 120% BEP.